## Start Here
Field Troubleshooting Calculators
Companion to: Instrumentation Troubleshooting: Loops, Transmitters & Valves
How to use | Yellow cells with blue text are inputs. Everything else is a formula. Overwrite the example values; do not type over formula cells.
Cal Record | As-found / as-left record for a 4-20 mA transmitter. Computes ideal output, error in % of span, PASS/FAIL vs tolerance, max error, and hysteresis.
Loop Check | Five-point hot loop check. Computes expected mA and engineering units (EU) at each point, deviation at the card and at the HMI, and PASS/FAIL.
mA Converter | mA to % and EU, EU to mA, plus a first-guess meaning of the reading (NAMUR NE43 bands). Includes a 5% step reference table.
Split-Half Log | Record each isolation measurement. Flags a step that eliminated nothing (the wrong measurement).
Formulas | % span = (I - 4) / 16 x 100. EU = LRV + ((I - 4) / 16) x (URV - LRV). I = 4 + 16 x (EU - LRV) / (URV - LRV). Error (% span) = (Measured mA - Ideal mA) / 16 x 100.
Alarm bands | NAMUR NE43: valid signal 3.8-20.5 mA; failure at or below 3.6 mA or at or above 21.0 mA. Vendor defaults vary (some 3.75 / 21.75 mA). Check the device's configured alarm levels.
Safety | These sheets do not authorize work. Follow your site's permit, LOTO, energized-work, and MOC procedures. Site procedure wins.

## Cal Record
As-Found / As-Left Calibration Record (4-20 mA output)
Example values shown: 0-100 psi pressure transmitter. Overwrite yellow cells.
Tag | PT-101 |  |  |  |  | Test standard
Device / S/N | Example DP/P xmtr |  |  |  |  | Std. cal due
LRV | 0 |  |  |  |  | Date
URV | 100 |  |  |  |  | Technician
Units | psi |  |  |  |  | Span | 100
Tolerance (± % span) | 0.5
As-found (record before any adjustment)
% Span | Input applied | Ideal mA | As-found mA | Error (% span) | In tol.
0 | 0 | 4 | 4.02 | 0.125 | PASS
25 | 25 | 8 | 8.05 | 0.3125 | PASS
50 | 50 | 12 | 12.11 | 0.6875 | FAIL
75 | 75 | 16 | 16.14 | 0.875 | FAIL
100 | 100 | 20 | 20.18 | 1.125 | FAIL
50 (down) | 50 | 12 | 12.15 | 0.9375 | FAIL
0 (down) | 0 | 4 | 4.05 | 0.3125 | PASS
Max as-found error (% span) |  |  | 1.125
Hysteresis at 50% (% span) |  |  | 0.25
Hysteresis at 0% (% span) |  |  | 0.1875
As-found result |  |  | FAIL
Action taken | Span trim | Pick from list. Re-ranging is not calibration.
As-left
% Span | Input applied | Ideal mA | As-left mA | Error (% span) | In tol.
0 | 0 | 4 | 4 | 0 | PASS
25 | 25 | 8 | 8.01 | 0.0625 | PASS
50 | 50 | 12 | 12 | 0 | PASS
75 | 75 | 16 | 16.02 | 0.125 | PASS
100 | 100 | 20 | 20.01 | 0.0625 | PASS
Max as-left error (% span) |  |  | 0.125
As-left result |  |  | PASS
Failure mode: adjusting before recording as-found destroys the evidence. Record first, then trim.

## Loop Check
Hot Loop Check: Five-Point Signal Injection
Inject at the field end, read at the card and the HMI. Example: 0-200 °C temperature loop.
Loop tag |  | TT-205
LRV |  | 0 |  | Fail direction | UP
URV |  | 200
Units |  | °C
Tolerance (± % span) |  | 0.5
% Span | Expected mA | Actual mA (card) | Expected EU | HMI reads (EU) | mA dev (% span) | HMI dev (% span) | Pass
0 | 4 | 4.01 | 0 | 0.1 | 0.0625 | 0.05 | PASS
25 | 8 | 8 | 50 | 50 | 0 | 0 | PASS
50 | 12 | 12.02 | 100 | 100.2 | 0.125 | 0.1 | PASS
75 | 16 | 16 | 150 | 150 | 0 | 0 | PASS
100 | 20 | 19.99 | 200 | 199.9 | -0.0625 | -0.05 | PASS
Overall | [6 empty] | PASS
Reading the result
1. mA dev bad, HMI dev matches it: problem is upstream of the card (injection, wiring, card input).
2. mA dev good, HMI dev bad: signal arrives correctly; suspect scaling (LRV/URV/units) in the controller.
3. Error same size at every point: zero/offset error. Error grows with signal: span error.
4. Failure mode: passing a loop check with damping hiding a slow card response. Let each point settle.

## mA Converter
mA / Engineering Units Converter
LRV | 0 | Reference table (5% steps)
URV | 150 | % Span | mA | EU
Units | in H2O | 0 | 4 | 0
|  | 5 | 4.8 | 7.5
mA to EU |  | 10 | 5.6 | 15
Measured current (mA) | 3.6 | 15 | 6.4 | 22.5
% of span | -2.5 | 20 | 7.2 | 30
Engineering units | -3.75 | 25 | 8 | 37.5
What it probably means | Low failure alarm (NE43) or supply/leakage problem | 30 | 8.8 | 45
Readings outside 4-20 mA give % below 0 or above 100 on purpose; the meaning column is the useful part. |  | 35 | 9.6 | 52.5
|  | 40 | 10.4 | 60
EU to mA |  | 45 | 11.2 | 67.5
Process value (EU) | 75 | 50 | 12 | 75
% of span | 50 | 55 | 12.8 | 82.5
Expected current (mA) | 12 | 60 | 13.6 | 90
Voltage across 250 ohm (V) | 3 | 65 | 14.4 | 97.5
|  | 70 | 15.2 | 105
|  | 75 | 16 | 112.5
|  | 80 | 16.8 | 120
|  | 85 | 17.6 | 127.5
|  | 90 | 18.4 | 135
|  | 95 | 19.2 | 142.5
|  | 100 | 20 | 150

## Split-Half Log
Split-Half Isolation Log
Measure in the middle of what is left. Each step should cut the suspect chain roughly in half.
| Tag | LT-301
| Links in chain at start | 7 | Process, sensor, transmitter, wiring, card, controller, display = 7
Step | Measure at | Expected | Actual | Good / Bad | Links before | Links after | Flag
1 | Field terminals / marshalling | 12.0 mA | 12.0 mA | Good | 7 | 4 | Good cut
2 | Transmitter terminals | 12.0 mA | 12.0 mA | Good | 4 | 2 | Good cut
3 | Transmitter local display vs process | 40% | 95% | Bad | 2 | 1 | Isolated
4
5
6
7
8
9
10
Fault isolated to |  | Process connection / wet leg (upstream of transmitter)
Verification